Ch 15: Fiber Optic Cable Pulling

# Avoiding Disaster

## Tensile stress (pulling load)

## Bending radius

# Despooling Cable

## Pull the cable to the side, not over the top of the reel

### Pull only from the strength member

### Avoids excessive force on the cable

#### That would stretch the jacket and cause fiber compression when the tension is released

#### Produces macrobends and attenuation

### Also avoids twists in the cable

# Microbends (not in textbook)

## Deviation of the core as measured from the axis of the fiber.

## Causes loss

### See links Ch_15a, Ch_15b

## Sources of stress can create microbends, such as:

### Irregularities during fiber manufacturing

### Manipulation of the fiber during cable manufacturing

### Installation operations and equipment (tie wraps, clamps)

### Environmental stresses (pressure, hits)

# Macrobends

## Bending the cable too tightly (violating the minimum bend radius)

## During pull – no less than 20 diameters

### Otherwise you can damage the cable

## Static – no less than 10 diameters

### Causes loss

# Pulling Force

## Usually 600 lb. for outside plant cable

## 300 lb or less for indoor cable

## Must not be exceeded

## Pull should be smooth, not jerky

## Pull on strength member only

# Test Cable Before Pulling

## Avoids quality problems and finger-pointing after installation

## Continuity is often enough

### Does it transmit light?

### Images from link Ch 15c

# Interference from Other Installations

## Ways to protect the fiber:

### Put it under other cables in duct

Put fiber in last, on top

Flashlight

(Continuity

Tester)

Visible Laser Tester

### Be careful about sharp edges in duct

#### Use innerduct

# Procedures for Pulling Cable

## Do long pulls from the middle

## Do very long pulls in stages with figure-8s

## Two ways to attach rope:

### Direct attachment to strength member

### Kellems grip to grab whole cable from outside

### Or both at once

#### Images from link Ch 15d

# Using the Kellems Grip

## Corning recommends using both the strength member and a Kellems grip to distribute tension

## Cover the grip with vinyl tape

### See link Ch 15e

# Puller Works Like a Capstan

## From Link Ch 15f

# Lubricant

## Use lubricant designed for the cable

## Avoid lubricating the part of the cable that will be handled

# Pull Speed

## Max. speed 2 mph when using rope

## You can pull 3 x as fast with measurement/pull tape than with rope because the rope cuts grooves in conduit

### Image from arncocorp.com (Link Ch 11f)

# Racking and Labelling

## “Rack” cable – lash it to the sides of a manhole or pull box with cable ties

## Attach cable ID tags anywhere people might see the cable

### State fiber core size, where it is accessible on both ends, and who the owner is

# Premises Cables

## They are more fragile than outdoor cables

### Avoid kinks and snags

## Heavy copper cables can put pressure on fiber sharing the same trays

### One solution is innerduct

### Innerduct with pull tape already installed is very easy to install

# Premises Cables

## Use cables with proper fire ratings

## Remove old cables

## Leave service loops – extra length

Ch 16: Fiber Optic Restoration

# Proactive Planning

## Designing a network that is reliable

## FDDI is reliable because it uses two counter-rotating rings

## “self-healing”

# Route Diversity

## More than one path for the data

## No single point of failure

## Increases network cost, but also increases reliability

# Faults at the Patch Panel

## Improper dressing of jumpers and cables

### Dressing the cable involves properly aligning and positioning the cables in a neat and orderly manner for termination

#### From Link Ch 16a

## Improper keying or dirty connectors

## Local damage

# Faults of System

## Under- or over-driving the optical transmission causes problems

### On LANs, under-driving is more likely (too many dB of loss)

### Some high-power laser sources can saturate the receiver if the network has too little loss

# Faults from Installation

## Improper bend radius

## Clamping too tight

## Dressing, termination, routing

# Faults from Construction

Backhoes digging up cable

# Typical Cable System Faults

## Aerial cables falling down

### Lightning, falling trees, etc.

## Cutting through walls or ceilings in LANs

# Equipment Used in Restoration

## Cleaning kit

## Microscope

## Light source and power meter

## Visual Fault Locator

### Bright laser VFLs are best for finding internal breaks

## OTDR

### Essential for outside plant work to locate faults

### Less common for LANs

#### High cost

#### Short networks

# Restoration Flow Chart

## First test power to receiver

## Then power from transmitter

## That will determine if the problem is in the electronics or the fiber

# Locating a Cable Plant Problem

## Use a VFL to locate the problem

### Sometimes you will see the red light escaping at a break or bad connection

### You can also just see how far down the cable plant the red light goes before it stops

## For longer runs, good documentation is extremely important so you can follow the cable route

# OTDR

## If a cable is over 500 m or underground, an OTDR may be necessary

## Use a launch cable to eliminate the dead zone

## Use the 850-nm range to get best distance resolution

# Restoring Service

## Protect repair points with closures or patch panels

### New hardware may be needed

## Can the system handle the added loss of the new connectors, splices, and cable length?

## Can you run a temporary span of cable through the ceiling, over the roof, etc. to restore service quickly?

# Storage Loops

## Buildings change a lot, so do networks

## Slack should be stored on the wall or ceiling, considering aesthetics and size

# Emergency Restoration (With Retrievable Slack)

## Use a VFL to find the break

### Test from both ends to make sure there is only one break

## Choose best point and method to repair fiber

### Pull cables back to ceiling, floor, post etc. for physical mounting

## Document the Repair

## Test the repaired span

# Emergency Restoration(No Retrievable Slack)

## Would it be quicker to pull in a new cable or segment?

## To repair, you must add in more cable

### Two termination points, double the labor and material

### New cable must have at least as many fibers as the existing cable

# Restoration for Singlemode Networks

## More difficult to repair than multimode networks

### Higher speeds and greater distances

### Cable is often buried, aerial-placed, or in long conduit

### Problem often caused by a natural disaster or construction work

### Many users are affected, large revenue losses

# Singlemode Restoration Suggestions

## Prioritize fibers – then fix most important fibers first

## Have a kit ready with spare connectors, connectorization kit, mechanical splices

## Have a trained restoration crew with emergency phone numbers

## Have test equipment and tools ready

# Restoring Service

## A single broken fiber can be replaced using a dark fiber (if one is available)

## Is there enough slack to make a repair point?

## Would replacing the span be easier, quicker, cheaper than repairing it?

## Install connectors or splice?

# Recommended Restoration Posture

## Document fiber routes

### Patch panel designations, signal type, interconnect routing

## Document transmitters’ and receivers’ power levels

### Both minimum and maximum power for detectors

## Document optical loss for all spans

### At both wavelengths (850/1300 nm for multimode and 1310/1550 nm for singlemode)

## Document fiber size and manufacturer

## Copies of OTDR traces (if any)

## Document actual cable length in meters or feet for each segment from cable markings

## Prioritize fibers

# Restoration Planning

## Flow of information – who detects the problem, and who do they call?

## Is an emergency restoration needed, or can we do a planned restoration

## Make sure you have records, kits, trained staff

## Prioritize your customer and fibers

## What is the time allowance for restoration?

## Temporary or permanent repair?  How much loss is tolerable?

## Arrange for communications between OTDR operators and splicers

# Restoration (Misc.)

## Keep the restoration plan and staff current

## Test existing dark fibers regularly

## Evaluate each cable segment for worst case failures

## Do you photograph/film your restorations? The use of film and/or pictures provides a good learning and review tool. In the case of litigation the pictures can be invaluable.

# Postrestoration

## Redocument and retest your splices, spans, and segments.

## Adjust your “as built” drawings

## Have a meeting to review all aspects of the restoration.

### What happened? What were the cause and impacts?

### What did we do well?

### What did not work? (Technique, equipment, products, staff)

### How can this be resolved?

### How can we improve?

### What needs to be done to rebuild kits and replenish inventory?

Color Codes (not in textbook)

## For loose-tube cables, both the individual fibers and the buffer tubes are color-coded

| TIA/EIA-598 Color Code ### Position | ### Color |
| --- | --- |
| ### 1 | ### Blue |
| ### 2 | ### Orange |
| ### 3 | ### Green |
| ### 4 | ### Brown |
| ### 5 | ### Slate |
| ### 6 | ### White |
| ### 7 | ### Red |
| ### 8 | ### Black |
| ### 9 | ### Yellow |
| ### 10 | ### Violet |
| ### 11 | ### Rose |
| ### 12 | ### Aqua |

# Cable Jacket Colors

## Cable jackets also have a color code, although not all manufacturers obey it

## Multimode indoor cable: orange

## Singlemode indoor cable: yellow

## Outdoor cable: black

## Laser-optimized: aqua

### See links Ch 16c, Ch 16d

Last modified 4-28-06